MSC/Circ.916

Ref. T4/4.01




 MSC/Circ.916

4 June 1999

INTERPRETATIONS OF THE INTERNATIONAL CODE FOR THE APPLICATION OF

FIRE TEST PROCEDURES (FTP CODE) AND FIRE TEST PROCEDURES

REFERREDTO IN THE CODE

1 The Maritime Safety Committee, at its seventy-first session (19 to 28 May 1999), approved, with

a view to ensuring uniform application of the fire test provisions of the FTP Code containing vague wording

which is open to diverging interpretations, the unified interpretations prepared by the Sub-Committee on

Fire Protection, at its forty-third session, as set out in the annex.

2 Member Governments are invited to use the annexed interpretations as guidance when applying

relevant provisions of the FTP Code for the testing of new materials tested on or after 21 May 1999, in

order to fulfil the requirements of the 1974 SOLAS Convention, and to bring these interpretations to the

attention of all parties concerned.

***
ANNEX

INTERPRETATIONS OF THE FTP CODE AND FIRE TEST PROCEDURES

REFERRED TO IN THE CODE

Part 2 - Smoke and toxicity test

Paragraph 2.6.2

Not only the FTIR (Fourier Transform Infrared Spectrometer) method but also other methods such

as GC/MS (Gas Chromatography/Mass Spectrometer) which can produce traceable results can be used for

the gas analysis.

Part 3 - Test for "A","B", and"F" class divisions

Paragraph 2.1 (paragraph 2.6.2.2 of resolution A.754(18))

"B" class doors should be fire tested in B class steel bulkheads of dimensions as stated in

paragraph 2.4.1 of resolution A.754(18), otherwise approval should be limited to the type of construction

in which the door was tested."

Paragraph 3.1

The calcium silicate board described as a dummy specimen specified in paragraph 3.3 of

resolution A.653(16) should be used as a standard substrate for adhesives.

Paragraph 1.7 of resolution A.754(18)

"B" class constructions should be tested without finishes. For constructions where this is not

possible, finishes should be included in the non-combustibility test of the construction.

Paragraph 1.2 of resolution A.754(18)

The thickness of insulation on the stiffeners need not be same as that of the steel plate.

Paragraph 4.1 of Appendix A.III and paragraph 4.1 of Appendix A.IV of resolution A.754(18)

Penetrations and transits should meet both integrity and insulation criteria.

________
